1.0	Manufacturers

A.	Available Manufacturers: Subject to compliance with requirements, Manufacturers offering products that may be incorporated in the work include, but are not limited to, the following:

1.	Amweld Building Products, Inc.

2.	Benchmark Commercial Doors.

3.	Ceco Door Products.

4.	Fenestra Corp.

5.	Metal Products Inc., Corbin, Kentucky.

6.	Steelcraft.

2.0	Doors

A.	All steel doors shall be 1-3/4-inch thick and of material per ANSI/SDI 100.

1.	Interior Doors shall be Grade II, Heavy-duty, full flush design, minimum 0.0478-inch thick cold-rolled steel sheet faces.

2.	Exterior doors shall be same as interior doors, and fully galvanized.

3.0	Frames

A.	All metal frames for doors, transoms, sidelights, borrowed lights, and other framed openings shall be supplied according to ANSI/SDI 100. All frames shall have concealed fasteners.  Fabricate frames of minimum 16 gauge cold-rolled steel.

1.	Fabricate all frames with mitered corners, continuously welded construction. "Knock-down" frames are not permitted except in applications to preserve wall finish such as glazed block. The Medical Center Facilities Planning and Construction office must approve the location for the "knock-down" frames.

2.	Frames for interior openings over 48 inches wide shall be 14 gauge steel.

B.	All single door frames shall have 3 door silences except frames with weather stripping.  Double door frames shall have two door silences on the head of the frame.

C.	All hollow metal frames shall be slushed full of grout.

D.	Exterior frames and frames in high moisture areas shall be fully galvanized.

E.	Except for frames located in existing concrete, masonry, or gypsum board assembly construction, place frames before constructing enclosing walls and ceilings.

F.	In new masonry construction, install at least 3 wall anchors per jamb, adjacent to hinge location on hinge jamb and at corresponding heights on strike jamb.  Acceptable anchors include masonry wire anchors and masonry T-shaped anchors.

G.	In metal stud partitions, install at least 3 wall anchors per jamb at hinge and strike levels.

H.	Install fire-rated frames according to NFPA 80.

4.0	Door Installation: Fit Hollow-metal doors accurately in frames, within Clearances specified in ANSI/SDI 100.

A.	Fire-Rated Doors: Install with clearances specified in NFPA 80.

B.	Smoke control doors: Comply with NFPA 105.