TYPE OF SPACE															MAXIMUM ACCEPTABLE

NOISE CRITERIA (NC) CURVE

GENERAL

CLASSROOMS/LIBRARIES													35

RESIDENCE-MULTIPLE OCCUPANT										35

BANQUET HALL/BALLROOMS												35

MUSEUM/DISPLAY AREA													35

LABORATORIES																40

RESTAURANT																	40

RECREATION HALLS															40

LOBBIES/HALLS/CORRIDORS												40

CAFETERIA																		45

RETAIL SPACE																	45

KITCHEN/LAUNDRY/GARAGE												45

RESTROOMS/LOCKER ROOMS											45

MEDICAL FACILITY

PATIENT ROOMS																25

OPERATING ROOMS/WARDS												35

WAITING ROOMS																40

OFFICES

BOARD ROOMS																25

CONFERENCE ROOMS														30

PRIVATE OFFICE/RECEPTION ROOMS									35

OPEN OFFICE/STUDIO														40

TABULATION/COMPUTATION												45

AUDITORIUMS

CONCERT HALLS/SOUND STUDIO										15

LEGITIMATE THEATER														25

MOVIE THEATER/LECTURE HALL										32

SPORTS CENTER

COLISEUM																		35

GYMNASIUM																	40

SWIMMING POOL																50