VALVES 2 1/2" AND SMALLER

SERVICE						GATE			GLOBE				BALL			CHECK

Chilled Water					150*				150*				150*				150*

*	Rated for 250 psig WOG working pressure

Domestic Hot and				150				150				150				150

Cold water

Heating Water 					---					150				150				150

Low and Medium				150				150				---					150

Pressure steam

and low pressure

steam condensate

High Pressure Steam			300**				300**				---					300**

High pressure steam

Condensate

**	Designed for 500 deg F steam at 300 psig

VALVES OVER 2 1/2"

SERVICE						GATE			GLOBE		BUTTERFLY	CHECK

Chilled Water					250*				250* 				250*				250*

*	Valves with ANSI 125/150 bolt pattern may be used if flanges and valves meet the 250 psig WOG design pressure.

Domestic Hot and				150				150				150				150

cold water

Heating Water				 	150				150				150				150

Low and Medium				150				150				 ---					150

Pressuresteam and

low pressuresteam

condensate

High Pressure Steam		 	300**				300**				 ---					300**

and High pressure

steam condensate

**	Rated for 500 deg F, 300 psig steam (cast steel)