MONITOR							DGP Requirement

HW Supply Temp							AI

HW Return Temp							AI

- TEMPERATURE CONTROL

Valve Pos CPA								AO

HW Pump 2A S/S							DO

HW Pump 2A Stat							DI

HW Pump 2B S/S							DO

HW Pump 2B Stat							DI

- SOFTWARE CONTROL

HW Supply temperature based on outdoor air reset schedule.

Initiate lead/lag operation on all pump pairs.

- NOTE:

The VAV pumps and reheat pumps, piping and valving shall be separate and independent of the unit ventilators and fan coil unit hot water zoning to allow the heating system to be automatically turned off in most of the building during summer months.

Parallel traps on condensate line from HW converter.

Pressure rating shall be 250 PSI min for all components.

Locate temp sensors such that if pumps are turned off, the high temp pop-off does not go off.