1.0	All exit signs shall be Lithonia Signature Series with LED (light emitting diodes) or equal.  The fixture shall have 3/4 inch letter stroke and have a green lens for the panel insert.  Red may be used on renovations to match existing exit signs.  The housing color shall be white.

2.0	Maximum power consumption shall be 2.5 watts per hour.

3.0	All exit signs shall be illuminated at all times, and be connected to the emergency power system.  Battery back-up units are permitted if an emergency power system is not available in the building.

4.0	The back-up battery shall be sealed, maintenance-free, nickel-cadmium type with a minimum 10 year nominal life.

5.0	The battery charger system shall be fully automatic, solid state, with constant current.